Issued March, 2015 				SECTION 07810

CEMENTITIOUS FIREPROOFING

PART  1 - GENERAL

1.00	SCOPE

  - This specification covers labor, materials, equipment, and application necessary for, and incidental to, the complete and proper installation of cementitious fire protection for application to steel structures and supports in accordance with all applicable requirements of contract documents.

    - This specification shall be supplemented by the applicable requirements of building codes, insurance rating organizations and all other authorities having jurisdiction.

  - SECTION INCLUDES

    - Cementitious fire protection material.

1.01	RELATED DOCUMENTS

A.  Drawings and general provisions of the contract documents, including Conditions of Division 1

apply to the work of this section.

1.02	DESCRIPTION OF WORK

A.  The work of this section shall include, but is not limited to:

1.  Interior fireproofing, concealed from view and direct contact

2.  Interior fireproofing, exposed to view and direct contact or abuse

3.  Exterior fireproofing, exposed to the elements and contact and possible abuse.

1.03	RELATED WORK

A.  Examine all of the contract documents for requirements which affect the work of this section.  Other specification sections, which directly relate to the work of this section include, but are not limited to the following:

1.  Fire Stopping			Division 07841

2.  Insulation				Division 07200

3.  Lath and Plaster			Division 09200

4.  Structural Steel			Division 05100

5.  Steel Joists				Division 05210

6.  Metal Floor Decking			Division 05311

7.  Metal Roof Decking			Division 05312

8.  Mechanical Div. 15			Re:  Patching

9.  Electrical Div. 16			Re:  Patching

10. Concrete				Division 03000

Page 1

1.04	QUALITY ASSURANCE

A.  Installer:  Contractor shall be approved by manufacturer, and be experienced in installing specified products, and is approved by the manufacturer of the fireproofing products.  A manufacturer's willingness to sell products to an installer engaged by contractor, does not in itself confer qualification on the buyer.

B.  Single Source:  Obtain spray applied fireproofing products from a single source for each product required.  Provide secondary materials, which are acceptable to the fireproofing manufacturer which, are included in the tested and/or listed designs.

C.  Fire Resistance:  Provide fireproofing materials that have been listed and classified by one or more of the following testing authorities: Underwriters Laboratories of Northbrook, IL and/or Underwriters Laboratories of Scarborough, Ontario; Warnock Hersey or other testing and inspecting agency acceptable to the architect and authorities having jurisdiction.

- Packaging:  All products must be packaged with proper identifications and approval indications acceptable to the testing and/or listing agency.

E.  Asbestos:  Manufacturer shall provide Certification that products supplied are 100% asbestos free.

F.   Steel Surfaces:  Structural steel and steel decking shall be unprimed.

G.  Painted Steel Surfaces:  Steel surfaces that require fireproofing and that are painted and/or primed, shall meet UL requirements for application and adhesion characteristics.  Provide certifications from fireproofing manufacturer of compatibility of fireproofing and painted systems.  Restrictions published by UL shall apply.

H.  Remedial Work:  Steel surfaces with incompatible primers or paint shall be remedied by removal of the primer or paint, be lathed, or otherwise remedied within the requirements of UL, so that adequate and approved bonding can occur, acceptable to authorities having jurisdiction.

1.05	PROJECT CONDITIONS

A.  Environmental Limitations:  Do not apply sprayed fireproofing material when ambient or substrate temperatures are 40 deg. F. (4 deg C) or lower, unless temporary heat and protection is provided to maintain temperatures at or above this level for 24 hours before, during and 24 hours after application of fireproofing.

B.  Ventilation:  Ventilate building spaces during and after application of fireproofing at a rate of four (4) air changes per hour until fireproofing is dry.  If natural ventilation is insufficient, employ mechanical means as necessary.

C.  Surfaces to be sprayed:  Surfaces to be sprayed must be free of any substance that would impair proper adhesion.

D.  The contractor shall make available to the fireproofing contractor suitable area(s) for permanent 	locations for mixing and pumping fireproofing.  This site must be:

1.  Convenient to the structure

2.  Be able to accommodate delivery of product

3.  Allow for space for truck storage and trailer parking, and for materials and equipment

- Be well drained

Page 2

5.  Be near a suitable source of potable water of quantity required

6.  Have a proper source of electrical power, if required.

- Provide temporary heat and ventilation to comply with manufacturer’ s recommendations

1.06	SEQUENCING

A.  Sequence and coordinate application of sprayed fireproofing with other related work specified in other Sections to comply with the following requirements:

- Provide temporary enclosure for interior applications to prevent deterioration of applied materials exposed to unfavorable environmental conditions.

- Avoid exposure of fireproofing to unnecessary damage or abrasion.

- Do not apply fireproofing to metal roof decking until roofing is complete including installation of all air handling systems.  Prohibit all roof traffic until application of fireproofing is completed and dry.

- Do not apply fireproofing until all hangers, clips and other necessary supports are in place, requiring penetration of fireproofing if installed after the application of fireproofing.

- Ducts, piping and other items that would interfere with the application of fireproofing shall not be installed, until application is completed.

1.07	APPLICATION PARAMETERS

A.  The fireproofing contractor shall be allowed to move freely to apply products as necessary.  Materials stored on the floor, shall be protected by the contractor, or relocated if these materials prevent the proper application of  fireproofing.

B.  Patching, repairing and cleaning of fireproofing, due to damage done by others, shall be performed by the fireproofing applicator.

C.   After completion of fireproofing, the fireproofing applicator shall remove all equipment, and broom sweep all floor areas of overspray materials.

D.  Application of fireproofing shall not commence until the project is at a stage to allow the applicator to apply product continuously and efficiently, without undue interference and delay by other trades.

E.  Conference:  Convene a pre-installation conference to establish a procedure to maintain optimum 	working conditions and to coordinate this work with related an/or adjacent work.

1.08	SUBMITTALS, REFERENCES AND APPLICABLE STANDARDS

A.  Product Data:  Submit manufacturer's product data, installation instructions, use and limitations for each material used, and applicable fire test designs, as listed by approved fire testing organization.

B. Performance Certification:  Submit manufacturer's verification of performance criteria, fire performance and compliance with applicable standards.

Page 3

C.  Applicable Standards and Test Methods:

Products submitted shall be tested in accordance with the following test methods:

1.	ASTM E119, Fire Test of Building Construction and Materials

2.  	ASTM E84, Test for Surface Burning Characteristics of Building Materials

3.  	ASTM E136, Behavior of Materials in a Vertical Tube Furnace at 750 Degrees C

4.        ASTM E605, Thickness and Density of Sprayed Fire Resistive Materials Applied to Structural Members

5.  	ASTM E736, Cohesion/Adhesion of Sprayed Fire Resistive Materials Applied to Structural Members

6.  	ASTM E759, Effect of Deflection of Sprayed Fire Resistive Materials Applied to Structural Members

7.  	ASTM E760, Effect of Impact on Bonding of Sprayed Fire Resistive Materials applied to Structural Members

8.       ASTM E761, Compressive Strength of Sprayed Fire Resistive Materials Applied to Structural Members

9.       ASTM E859, Air Erosion of Sprayed Fire Resistive Materials Applied to Structural Members

10.	ASTM E937, Corrosion of Steel By Sprayed Fire Resistive Materials Applied to Structural Members

11. 	AWCI Technical Manual 12-A, Standard Practice for the Testing and Inspection of Field Applied Sprayed Fire-Resistive Materials; an Annotated Guide

12.        ASTM G21, Determining Resistance of Synthetic Polymeric Materials to Fungi

1.09	WARRANTY

A.  General Warranty:  Submit a written warranty, executed by the contractor and cosigned by the installer, agreeing to repair or replace sprayed fireproofing materials that fail within the specified warranty period.

1. Failures include, but are not limited to cracking, flaking, eroding in excess of specified requirements, peeling and delaminating of sprayed fireproofing from substrates due to defective materials or installation.

2.  Not covered in this warranty are failures due to damage by others, such as occupants and owner maintenance personnel, exposure to environmental conditions other than those investigated and approved during fire-response testing, excessive flexing of floor systems, and work on said roof systems, and other causes not reasonable foreseeable under conditions of normal use.

B.   Warranty Period:  1 years, from date of substantial completion.

  - DELIVERY, STORAGE AND HANDLING

  - Deliver materials to the project in manufacturer’s unopened packages, fully identified as to trade name, type, and other identifying data.  Packaging shall bear the ULI or ITS labels and seals for fire resistance ratings.

  - Store materials at a temperature above 40 degrees F (4 degrees C) in a dry location, protected from the weather.

  - Damaged packages found unsuitable for use and any materials which have come into contact with contaminants prior to use shall be rejected and removed from the project.

## PART 2 - PRODUCTS

A.  General:  All products shall be cementitious fireproofing materials.  Physical properties shall be in accordance with below listed properties.  Products shall be a mixture of gypsum and/or cement based 	materials, with lightweight aggregates to be mixed with water to form a slurry for conveyance and application.  Mineral fiber based products are not permitted.

Page 4

2.01	Concealed Cementitious Fireproofing: Concealed, meeting the below listed minimum physical properties, for use in locations not subject to physical contact or abuse.

A.  Cementitious Manufacturers:

1.  Carboline / Southwest Fireproofing Products, Type 5GP(, P-15

2.  or equal

B. Physical Properties: Minimum values unless otherwise indicted, or higher values required to attain designated fire resistance ratings, measured per standard ASTM test methods referenced above in section 1.08, Part C.

1.  E 84:  		Flame Spread  0, and Smoke Developed  0.

2.  E 136:		Passes, and is determined to be non-combustible

3.  E 605:		Density shall be a minimum of 15 pcf.

4.  E 736:		Cohesion/Adhesion shall be 200 psf average, with 150 psf

minimum acceptable level; if primed steel is used, comply with

requirements published by U.L.I.

5.  E 759:		No cracking, spalling or delamination

6.  E 760:		Impact:  No delamination, cracking or spalling

7.  E 761:		Compression shall be 5.0 lb/sq. in.

8.  E 859:		Erosion shall be 0.00 g/sq.ft., maximum

9.  E 937:		Corrosion:  No evidence of corrosion permitted

10.  G 21:		Mold Resistance: No evidence of growth

C.  Structural members not meeting minimum size requirements specified in a design shall receive an adjusted thickness of fireproofing consistent with the member's W/D ratio.

2.02 	Exposed Fireproofing:    For exposed interior applications of sprayed fire-resistive materials, provide manufacturers standard products complying with requirements for materials and composition having the following minimum physical properties measured per ASTM standard test methods referenced above in Section 1.08, Part C.

1.  E 84:		Flame Spread 0, and Smoke Developed 0

2.  E 136:		Passes, and is determined to be non-combustible

3.  E 605:		Density shall be a minimum of 22 pcf.

4.  E 736:	Cohesion/Adhesion shall be >400 psf average for products with a minimum density of 22 pcf, and 1000 average psf for products with density above 35 pcf.

5.  E 759:		No cracking or delamination

6.  E 760:		Impact:  No delamination, cracking or spalling

7.  E 761:	Compression shall be 100 psi for products with a minimum density of 22 pcf, and 300 psi for products with densities over 35 pcf.

8.  E 859:		Erosion shall be 0.00 g/sq.ft., maximum

9.  E 937:		Corrosion:  No evidence of corrosion permitted

10.  G 21:		Mold Resistance: No evidence of mold growth

A.  Exposed fire protection is intended for, but is not limited to the following areas:

1.  Stairwell columns and beams

2.  Elevator shafts structural steel

3.  Mechanical room columns

4.  Areas where physical abuse may be encountered

Page 5

B.  Cementitious Manufacturers:

    - Carboline / Southwest Fireproofing Types 5MD( for regular conditioned areas; 7GP( for humidity conditions,

    - P-239 for fire protection and acoustical value

    - Type 7HD( for high density interior application

    - or equal

2.03 	Exterior Fire Protection:   Exterior fire protection shall be defined as permanently exposed to weather, and shall be manufactured of cement based products, with light weight aggregate, with a minimum density of 40 pcf., and shall have the minimum ASTM values given above for the exposed fire protection in section 2.02 of this specification.

A.  Cementitous Manufacturers:

- Carboline Types Pyrocrete 40, Pyrocrete 240 High Yield and Pyrocrete 241 Series

- or equal

2.04	Miscellaneous Materials:   Provide the following materials as standard with each of the fireproofing systems, as recommended by the manufacturer for each condition and substrate.

A.  Primers:  It is not recommended that any structural steel primers be used on any steel surfaces, unless 	tested and listed by ULI in designs proposed to be used.  Compatible primers may be used, providing the fireproofing manufacturer can verify such compatibility in accordance with UL requirements.

B.  Adhesives:  Provide adhesives as necessary, to comply with manufacturer requirements for adhesion of fireproofing.  Acceptable adhesives are:

1.  TC 55 water based acrylic adhesive

2.  Type DK Spatter Coat

C. Reinforcements:  Provide fiberglass mesh or wire lath for areas where adhesion is not compatible and for application of fireproofing to steel joists.

D. Mold Inhibitor:  Provide factory added mold inhibitor tested in accordance with ASTM G21 for areas such as hospitals, testing laboratories, health facilities and other areas of hygienic requirements.

E. Top Coats:  Use as required and recommended by fireproofing manufacturer or compatible products.

### PART 3 – EXECUTION

3.01	Pre-Installation Examination:  The applicator and the contractor shall examine surfaces to be fire protected, and determined if the surfaces are satisfactory.  Substrate conditions must comply with the following:

A.  Substrates must be free of grease, oil, rolling compounds, incompatible primers, loose mill scale, dirt or any other foreign matter which would prevent proper bonding of fireproofing.

Structural steel shall be unprimed.  Steel roof and floor decking shall be galvanized only.

B.  Any objects such as hangers, piping attachments, and other suspended retainer devices shall be properly secured.

Page 6

  - Ducts, piping, and other equipment shall not be placed or suspended until the Fire protection materials are in place.

3.02	Preparation:

A.  Clean any substrate not ready to receive fireproofing. Consult with manufacturer if conditions exist that are not easily remedied.

B.  Apply adhesives as necessary.

C.  Cover all work subject to overspray during application.  Provide temporary enclosure when necessary to temporarily confine fireproofing and protect the environment.

D.  Assure maintenance of ambient temperatures, and/or heat and ventilation when required.

  - Mock Up

  - Before proceeding with the work, the applicator shall apply the fire protection material to a section as a mock up.  This section shall be witnessed by the architect or owner’s representative and shall be subject to their approval to be used as a guide for texture, and thickness of the finish work.

3.04	Installation, General

A.  Comply with manufacturers written application instructions and procedures for mixing, conveying and applying products, in accordance with the types of recommended equipment, admixtures and specific procedures regarding special conditions.

- Coat substrates with adhesives if necessary.

C.  Extend fireproofing materials in full thickness per approved design, to be protected.  Unless otherwise recommended, install fireproofing complete in each area, prior to another.

D.  Provide a uniform surface matching UL requirements for designs approved.  Apply products at the minimum densities required, or greater.

E.  Cure fireproofing to prevent premature drying; protect from freezing as listed in Section 1.05 of this specification.

F.  Exposed to View Applications: Where exposed to view, provide appearance of Fire protection as follows:

1.  Provide a troweled surface of appearance previously determined prior to installation

2.  Surfaces shall be within tolerances of 1/16 inch

3.  Mask edges of terminations so as to achieve neat and sharp edges.

3.05	Field Quality Control:

A. Testing Agency:  The owner shall engage and the contractor and applicator shall approve a qualified independent testing agency to perform field quality inspections of applied fireproofing, and prepare reports.

1.  Testing shall be done in accordance with the AWCI’s "Technical Manual 12 - A, Standard Practice for the Testing and Inspecting of Field Applied Sprayed Fire - Resistive Materials" and ASTM E605.

- Tests shall be performed on thickness, density and adhesion

Page 7

3.  Variances shall be corrected with the testing agency present, and while the applicator is performing work in the same area to allow for expedient corrections.

4.  A schedule of tests to be performed shall be agreed upon by applicator, contractor and testing agency.

3.06	Cleaning and Repair:

A.  After completion of each day’s work, the applicator shall broom clean the area fireproofed.  Areas not to receive fireproofing but are finished surfaces shall be masked.

B.  All patching of damaged fireproofing shall be completed by applicator.

3.07	Schedule:

A.  Fire resistance rating(s) shall be in hours as listed below

STRUCTURAL COMPONENT		HOURS REQUIRED		UL DESIGN

________________________________________________________________________

FLOOR ASSEMBLY			______________________________________

ROOF ASSEMBLY			______________________________________

COLUMNS, SPANDREL		______________________________________

COLUMNS, INTERIOR			______________________________________

PRIMARY BEAMS			______________________________________

SECONDARY BEAMS			______________________________________

TRUSSES				______________________________________

ROOF DECK, BEAMS, JOISTS		______________________________________

B. List below other provisions not covered above: _______________________________________

3.08       Restrained and Unrestrained Conditions

Guidance information for determining conditions of thermal restraint in buildings is available in the introductory section of ULI’ s Fire Resistance Directory – Volume 1,  and in the in the Appendix of the test standards ASTM E119 and ANSI/UL 263.

The International Building Code (IBC), 2006, states, “Fire-resistance-rated assemblies tested under ASTM 	E119 shall not be considered to be restrained unless evidence satisfactory to the building official is furnished by the registered design professional showing that the construction qualifies for a restrained classification in accordance with ASTM E119. Restrained construction shall be identified on the plans.”

Definition

Thermal Restraint in Buildings: “Floor ceiling and roof-ceiling assemblies and individual beams in buildings shall be considered restrained when the surrounding or supporting structure is capable of resisting substantial thermal expansion throughout the range of anticipated elevated temperatures. Constructions not complying with this definition are assumed to be free to rotate and expand and shall be therefore considered as unrestrained.”                                         ANSI/UL263, Appendix C

END OF THIS SECTION

Page 8